## Sheet1
Calculation Formula for H₂SO₄ Dosing Prior to RO
Serial number | Name |  |  | Numerical value
1 | Coefficient 1 |  |  | 0.00080328
2 | Coefficient 2 |  |  | 49
3 | Flow rate（m3/h）Q |  |  | 15.4
4 | Alkalinity（mg/l)M |  |  | 189
5 | H₂SO₄ concentration (% w/w) n |  |  | 30
6 | H₂SO₄ density (g/cm³)ρ |  |  | 1.219
7 | Raw water pH a |  |  | 6.7
8 | pH b |  |  | 5.5
9 | H₂SO₄ flow rate for alkalinity removal X1（L/h） |  |  | 6.3933
10 | H₂SO₄ flow rate for pH adjustment X22（L/h） |  |  | 0.00039698
11 | Total H₂SO₄ dosing flow X（L/h） |  |  | 6.3937
| Chemical tank volume（L） (based on 7 days dosing) |  |  | 1074.1379
Calculation Formula for NaOH Dosing Prior to Post-RO Degassing Tower
Serial number | Name |  |  | Numerical value
1 | Coefficient 1 |  |  | 40
3 | Flow rate（m3/h）Q |  |  | 39.3
5 | NaOH concentration (% w/w)（%）n |  |  | 0.3
6 | NaOH density（g/cm3）ρ |  |  | 1.328
7 | RO permeate pH a |  |  | 6
8 | pH after caustic dosingpH b |  |  | 8.5
11 | NaOH dosing flow X（L/h） |  |  | 0.52234
| Chemical tank volume（L） (based on 7 days dosing) |  |  | 87.7536
Calculation Formula for PAC Dosing Before Sand Filtration and Antiscalant Dosing Prior to RO
Serial number | Name |  |  | Numerical value
1 | Flow rate（m3/h）Q |  |  | 53
2 | PAC concentration（%）n |  |  | 50
3 | Dosing concentration（mg/L）m |  |  | 3
4 | PAC dosing flow X（L/h） |  |  | 0.318
| Chemical tank volume（L） (based on 7 days dosing) |  |  | 53.424
Calculation Formula for Pre-treatment Filter Sizing in Purified Water Systems
Serial number | Equipment Name |  | Design flow（m3/h）Q | Design filtration velocity（m/h）v | Vessel diameter（mm）Φ | Backwash flow（m3/h） | Backwash velocity（m/h）q | Design pipe velocity（m/s）v1 | Design pipe velocity（m/s）v2 | Inlet and outlet pipe diameter（mm）DN |  | Anti-scaling water pipe diameter（mm）DN
1 | Multimedia Filter (Sand) |  | 53 | 10 | 2598.3826 | 159 | 30 | 1.5 | 2 | 96 | 111
2 | Activated Carbon Filter |  | 95 | 15 | 2840.412 | 126.6667 | 20 | 2 | 2.5 | 115 | 129
3 | Water Softener |  | 95 | 30 | 2008.4746 | 95 | 30 | 2 | 2.5 | 115 | 129
| Remarks： |  |  |  | Penetration depth（mm） |  | 541.6494
| 1、0〈Q≤45时，v1=1，v2=2； |  |  |  | Filtration rate（m/h） |  | 10
| 2、45〈Q≤80时，v1=1.5，v2=2； |  |  |  | Effective media size（mm） |  | 3
3、80〈Q≤150时，v1=2，v2=2.5；
Stainless Steel (Carbon Steel) Pipe Unit Price per Length Calculation
Serial number | Name | Numerical value |  | Nominal dimension
1 | Nominal inner diameter（mm）DN | 250 |  |  | DN15 | DN25 | DN32 | DN40 | DN50 | DN65 | DN80 | DN100 | DN125 | DN150 | DN200 | DN250
2 | Nominal outer diameter（mm）Φ | 273 |  |  | Φ20 | Φ32 | Φ38 | Φ45 | Φ57 | Φ76 | Φ89 | Φ108 | Φ133 | Φ159 | Φ219 | Φ278
3 | Density（kg/m3）ρ | 7.9
4 | Market price（CNY/kg） | 7
5 | Unit pipe price per meter（CNY） | 499.2208
|  |  | 100 |  | 150 | 0.471
108
7.9
7
9.9224
Note on C52: Common: 切勿改动或是输入数值！！！！
Note on D59: Common: 切勿改动或是输入数值！！！！
Note on E11: Common: 切勿改动或是输入数值！！！！
Note on E12: Common: 切勿改动或是输入数值！！！！
Note on E13: Common: 切勿改动或是输入数值！！！！
Note on E14: Common: 切勿改动或是输入数值！！！！
Note on E24: Common: 切勿改动或是输入数值！！！！
Note on E25: Common: 切勿改动或是输入数值！！！！
Note on E32: Common: 切勿改动或是输入数值！！！！
Note on E33: Common: 切勿改动或是输入数值！！！！
Note on F37: Common: 切勿改动或是输入数值！！！！
Note on F38: Common: 切勿改动或是输入数值！！！！
Note on F39: Common: 切勿改动或是输入数值！！！！
Note on G37: Common: 切勿改动或是输入数值！！！！
Note on G38: Common: 切勿改动或是输入数值！！！！
Note on G39: Common: 切勿改动或是输入数值！！！！
Note on H7: Common: 附加函数 请勿删除！！！！
Note on K37: Common: 切勿改动或是输入数值！！！！
Note on K38: Common: 切勿改动或是输入数值！！！！
Note on K39: Common: 切勿改动或是输入数值！！！！
Note on L37: Common: 切勿改动或是输入数值！！！！
Note on L38: Common: 切勿改动或是输入数值！！！！
Note on L39: Common: 切勿改动或是输入数值！！！！