## RO System LSI Value and Chemica
RO System Parameters and Water Quality Data | [7 empty] | LSI Calculation Based on Measured Concentrate Water Data |  |  | Hyde RO Membrane – Theoretical Antiscalant Dosage
RO System Parameters |  |  | Water Quality Data |  |  |  |  | 公式数据 |  |  | LSI RangeLSI | Dosage | Unit
Project | Parameter | Unit | Water Quality Project | Make-up Water | Concentrated water | Theoretical Concentrate | Unit | Lookup Project | Water Quality Data | Lookup Value | 0.3＜LSI＜1.0 | 3 | ppm
Feed Flow | 130 | M3/H | PH | 7.8 | 9 | 8.9053 |  | TDS Coefficient-A | 647.77 | 00.180 | 1.0＜LSI＜1.8 | 4 | ppm
Permeate Flow | 100 | M3/H | Conductivity | 272 | 1178.67 | 1178.6667 | us/cm | Temperature Coefficient-B | 25 | 1.98 | 1.8＜LSI＜2.8 | 5 | ppm
Concentrate Flow | 30 | M3/H | TDS | 331.2 | 647.77 | 1435.2 | mg/l | 钙硬系数-C | 658.93 | 2.82 | 2.8＜LSI＜3.2 | 6 | ppm
Feed Pressure | 1.2 | MPa | Ca2+ | 74.15 | 658.93 | 321.3167 | mg/l | M-Alkalinity Coefficient -D | 477.14 | 2.68
First-Stage Pressure | 1.15 | MPa | Total Hardness | 220.2 |  | 954.2 | mg/l | Calculation Results |  |  | Antiscalant Dosing Equipment Parameters
Second-Stage Pressure | 1.1 | MPa | M-Alkalinity | 95.1 | 477.14 | 412.1 | mg/l |  |  |  | Equipment Name | Parameter | Unit
Concentrate Pressure | 1 | MPa | CL- | 11.34 |  | 49.14 | mg/l | PHs | 6.36 |  | Chemical Tank Volume | 200 | L
Feedwater Temperature | 25 | ℃ | Si032- |  |  | 0 | mg/l | LSI | 2.64 |  | Metering Pump Flow Rate (Measured) | 10 | L/H
Feedwater Conductivity | 380 | us/cm | SO42- |  |  | 0 | mg/l |  |  |  | RO System Operating Time | 24 | H/Day
Permeate Conductivity | 8.5 | us/cm | Mg2+ |  |  | 0 | mg/l | LSI Calculation Using Theoretical Concentrate Data |  |  | Dosing Concentration | 5 | ppm
Concentrate Conductivity |  | us/cm | [5 empty] | Formula data
脱盐率Salt Rejection | 99.5 | % | [5 empty] | Lookup Project | Water Quality Data | Lookup Value | Theoretical Chemical Dosing Data
SDI15 Value | 3 | [6 empty] | TDS Coefficient-A | 1435.2 | 0.215 | Project | Data | Unit
Recovery Ratio（0.00） | 0.76923 | Decimal representation | [5 empty] | Temperature Coefficient-B | 25 | 1.98 | Hourly Chemical Consumption | 0.65 | kg/H
Concentration Factor | 4.3333 | [6 empty] | Calcium Hardness Coefficient – C Value | 321.3167 | 2.51 | Daily Chemical Consumption | 15.6 | kg
[8 empty] | M-Alkalinity Coefficient -D | 412.1 | 2.61 | Stock Solution Mass | 13 | kg
[8 empty] | Calculation Results |  |  | Dosing Preparation Frequency | 0.83333 | Day
[8 empty] | PHs | 6.775 |  | Note: Required RO Chemical Stock Solution |  | 13
[8 empty] | LSI | 2.1303 |  | kgDiluted to Chemical Tank Volume | 200 | L
Note: Hardness and alkalinity in Water Quality Data expressed as CaCO₃ equivalent
0 | →→→→ | Data to be entered manually
0 | →→→→ | Data automatically calculated by software (non-editable)
0 | →→→→ | Data to be entered manually from lookup tables (“ABCD coefficients”)
1.98

## LSI Value A, B, C, D Coefficien
Reference Table of A, B, C, D Values Required for LSI Calculation
Coefficient Table for A Value
TDS/mg/L | 45 | 60 | 80 | 105 | 140 | 175 | 220 | 275 | 340 | 420
A | 0.07 | 0.08 | 0.09 | 0.1 | 0.11 | 0.12 | 0.13 | 0.14 | 0.15 | 0.16
TDS/mg/L | 520 | 640 | 800 | 1000 | 1250 | 1650 | 2200 | 3100 | 4000-13000
A | 0.17 | 0.18 | 0.19 | 0.2 | 0.21 | 0.22 | 0.23 | 0.24 | 0.25
Coefficient Table for B Value
Water Temperature/℃ | 0.17: Mantissa (Decimal Part)
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
0 | 2.6 | 2.57 | 2.54 | 2.52 | 2.49 | 2.47 | 2.44 | 2.42 | 2.39 | 2.37
10 | 2.34 | 2.31 | 2.29 | 2.26 | 2.24 | 2.21 | 2.19 | 2.16 | 2.14 | 2.11
20 | 2.09 | 2.07 | 2.05 | 2.02 | 2 | 1.98 | 1.96 | 1.94 | 1.92 | 1.9
30 | 1.88 | 1.86 | 1.84 | 1.83 | 1.81 | 1.79 | 1.78 | 1.76 | 1.74 | 1.73
40 | 1.71 | 1.7 | 1.68 | 1.66 | 1.65 | 1.63 | 1.61 | 1.6 | 1.58 | 1.57
50 | 1.55 | 1.53 | 1.52 | 1.5 | 1.49 | 1.48 | 1.46 | 1.44 | 1.43 | 1.42
60 | 1.4 | 1.39 | 1.37 | 1.36 | 1.35 | 1.33 | 1.32 | 1.31 | 1.29 | 1.28
70 | 1.27 | 1.26 | 1.25 | 1.24 | 1.23 | 1.22 | 1.21
Combined Coefficient Table for C and D Values
Calcium Hardness or Alkalinity | 0.17: Mantissa (Decimal Part)
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
0 |  | 0 | 0.3 | 0.48 | 0.6 | 0.7 | 0.78 | 0.85 | 0.9 | 0.95
10 | 1 | 1.04 | 1.08 | 1.11 | 1.15 | 1.18 | 1.2 | 1.23 | 1.26 | 1.28
20 | 1.3 | 1.32 | 1.34 | 1.36 | 1.38 | 1.4 | 1.41 | 1.43 | 1.45 | 1.46
30 | 1.48 | 1.49 | 1.51 | 1.52 | 1.53 | 1.54 | 1.56 | 1.57 | 1.58 | 1.59
40 | 1.6 | 1.61 | 1.62 | 1.63 | 1.64 | 1.65 | 1.66 | 1.67 | 1.68 | 1.69
50 | 1.7 | 1.71 | 1.72 | 1.72 | 1.73 | 1.74 | 1.75 | 1.76 | 1.76 | 1.77
60 | 1.78 | 1.79 | 1.79 | 1.8 | 1.81 | 1.81 | 1.82 | 1.83 | 1.83 | 1.84
70 | 1.85 | 1.85 | 1.86 | 1.86 | 1.87 | 1.88 | 1.88 | 1.89 | 1.89 | 1.9
80 | 1.9 | 1.91 | 1.91 | 1.92 | 1.92 | 1.93 | 1.93 | 1.94 | 1.94 | 1.95
90 | 1.95 | 1.96 | 1.96 | 1.97 | 1.97 | 1.98 | 1.98 | 1.99 | 1.99 | 2
100 | 2 | 2 | 2.01 | 2.01 | 2.02 | 2.02 | 2.03 | 2.03 | 2.03 | 2.04
110 | 2.04 | 2.05 | 2.05 | 2.05 | 2.06 | 2.06 | 2.06 | 2.07 | 2.07 | 2.08
120 | 2.08 | 2.08 | 2.09 | 2.09 | 2.09 | 2.1 | 2.1 | 2.1 | 2.11 | 2.11
130 | 2.11 | 2.12 | 2.12 | 2.12 | 2.13 | 2.13 | 2.13 | 2.14 | 2.14 | 2.14
140 | 2.15 | 2.15 | 2.15 | 2.16 | 2.16 | 2.16 | 2.16 | 2.17 | 2.17 | 2.17
150 | 2.18 | 2.18 | 2.18 | 2.18 | 2.19 | 2.19 | 2.19 | 2.2 | 2.2 | 2.2
160 | 2.2 | 2.21 | 2.21 | 2.21 | 2.21 | 2.22 | 2.22 | 2.22 | 2.23 | 2.23
170 | 2.23 | 2.23 | 2.24 | 2.24 | 2.24 | 2.24 | 2.25 | 2.25 | 2.25 | 2.25
180 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.27 | 2.27 | 2.27 | 2.27 | 2.28
190 | 2.28 | 2.28 | 2.28 | 2.29 | 2.29 | 2.29 | 2.29 | 2.29 | 2.3 | 2.3
200 | 2.3 | 2.3 | 2.31 | 2.31 | 2.31 | 2.31 | 2.31 | 2.32 | 2.32 | 2.32
Calcium Hardness or Alkalinitymg/L | Mantissa (Decimal Part)
| 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90
200 |  | 2.32 | 2.34 | 2.36 | 2.38 | 2.4 | 2.41 | 2.43 | 2.45 | 2.46
300 | 2.48 | 2.49 | 2.51 | 2.52 | 2.53 | 2.54 | 2.56 | 2.57 | 2.58 | 2.59
400 | 2.6 | 2.61 | 2.62 | 2.63 | 2.64 | 2.65 | 2.66 | 2.67 | 2.68 | 2.69
500 | 2.7 | 2.71 | 2.72 | 2.72 | 2.73 | 2.74 | 2.75 | 2.76 | 2.76 | 2.77
600 | 2.78 | 2.79 | 2.79 | 2.8 | 2.81 | 2.81 | 2.82 | 2.83 | 2.83 | 2.84
700 | 2.85 | 2.85 | 2.86 | 2.86 | 2.87 | 2.88 | 2.88 | 2.89 | 2.89 | 2.9
800 | 2.9 | 2.91 | 2.91 | 2.92 | 2.92 | 2.93 | 2.93 | 2.94 | 2.94 | 2.95
900 | 2.95 | 2.96 | 2.96 | 2.97 | 2.97 | 2.98 | 2.98 | 2.99 | 2.99 | 3