## Sheet1
Chemical Dosing for RO Cleaning System
Serial number. | Project | Unit | Specification |  | Quantity | Volume（m3） | Water-holding ratio | Water capacity (m³)
|  |  | Diameter(m) | Length(m)
1 | Pressure Vesse | 个 | 0.202 | 2.503 | 5 | 0.080174 | 0.7 | 0.28061
2 | Piping | 个 | 0.05 | 50 | 1 | 0.098125 | 1 | 0.098125
3 | Security Filter | 个 | 0.3 | 1 | 1 | 0.07065 | 0.95 | 0.067117
5 | CIP Tank Total VolumeCIP | [6 empty] | 0.44585
6 | Adjusted for Design Factors | [5 empty] | 1.2 | 0.53502
7 | Effective CIP Tank Water VolumeCIP |  |  |  |  | 0.5
| Total | [6 empty] | 1.035
| Selected CIP Tank Volume | [6 empty] | 1.5
8 | Cleaning Flow Rate | m3/h | 34.0-45.5（One-time cleaning for 5 pressure vessels）
9 | Cleaning Chemicals |  |  | Chemical dosage ratio |  | Chemical dosage(L)
|  | MCT103 |  | 0.02 |  | 20.7004
|  | MCT511 |  | 0.02 |  | 20.7004