## Power Equipment System Descript
Utility Equipment Summary 2011.08.29
Number | System and Equipment | Specifications and Parameters | Remarks
1 | CDA (Compressed Dry Air) Main SystemCDA | 1.Air Compressor: Brand Atlas COPCO; Model GA160-8.5; Cooling Type: Air-cooled; Operating Pressure: 0.6–0.85 MPa; Capacity: 28.92 m³/min; Motor Power: 160 kW | Originally, 4 air compressors were installed (4 independent CDA treatment lines manifolded into the main header and distributed to the workshop). Currently, only 2 compressors are in operation.
2.Refrigerated Air Dryer: Brand UF; Model RD-30HA; Capacity: 32 Nm³/min; Power Consumption: KW
3.Desiccant Air Dryer: Brand UF; Model MAD-30; Capacity: 32 Nm³/min; Motor Power: KW
2 | Chilled Water System | 1.Chiller Unit: Brand McQuay; Cooling Capacity: 2109.6 kW (≈599 RT) | Three chiller units are installed, including chilled water pumps, cooling water pumps, and cooling towers. Make-up water for both chilled water and cooling water systems is supplied from the RO Water Treatment System. The chilled water is used for cooling and heating exchange in the MAU system and fan coil units, while another loop, via a plate heat exchanger, supplies process cooling water to various equipment.
2.Circulating Water Pump: Brand Jiangqing; Power 75 kW; Voltage 380 V; Power Factor 0.85
3.Cooling Water Tower: Brand: ____; Specification: ____
3 | Cleanroom & HVAC System | 1.The air supply system consists of 9 MAUs (Make-up Air Units) with a total airflow capacity of 766,330 m³/h. Cooling and heating energy are supplied by the chilled water system and the steam system (hot water provided via steam heat exchangers). In addition, the humidification system is supplied by steam. | 1.MAU fans draw in fresh air, passing through pre-filter, medium, and HEPA filters, then across heating/cooling coils before supply to cleanrooms. Return air from clean zones is routed back to MAU pre-filtration stage for secondary circulation.
4 | RO Water Treatment System | RO Water Treatment Process Flow:
Raw Water
Booster Pump
RO System
Booster Pump
Permeate Water Storage Tank
Permeate Water Storage Tank
Cartridge Filter
Chilled Water System Make-up Water
Hot Water Boiler Make-up Water
Cooling Water System Make-up Wate

## Production Equipment Energy Con
Production Equipment Overview Statement 2011.08.29
Number | Description | Equipment Composition | Process Flow and Utility Requirements
1 | Automatic Glass Loading Section | 1. Automatic Glass Loader 2. Automatic Transfer Conveyor 3. Glass Edge Grinding Machine 4. Glass Washing Machine | The automatic glass loader first transfers the glass sheets onto the automatic transfer conveyor. After edge grinding, the sheets are washed, then undergo a second edge grinding process, followed by a final wash before entering the next process stage. The required utility connections for this section are:1.Power supply: 3-phase, 5-wire,2.Compressed Dry Air (CDA): DN50 (1"), 0.8 MPa.3.Piping: SUS304 stainless steel, WDI Ø50 mm.4.Feedwater: 1" PVC pipe;Drainage: wastewater discharged to the wastewater treatment station tank, treated and recycled for reuse.
2 | Pre-process Glass Washer Wastewater Treatment | Collection Tank / Pump / Water Treatment System (Chemical Dosing for Coagulation & Precipitation) | Wastewater from the glass washer is collected and conveyed to the sedimentation basin. An oil-water pump transfers the wastewater under pressure to the treatment system, where coagulants are dosed for clarification and separation. Reclaimed water is stored in the reclaimed water tank and pressurized for reuse in the washer. Reject water is discharged to the wastewater treatment station or other designated disposal.
Special Note:The automatic loader first transfers raw material (finished glass sheets) onto the conveyor. The conveyor automatically feeds the sheets into the edge grinding machine. After edge processing, the sheets are automatically conveyed to the washing machine for cleaning. Upon completion, the cleaned sheets are transferred by the conveyor to the next process.

## PECVD Backup Energy Configurati
Equipment Configuration Descriptio 2011.08.30
Number | Equipment Area | Equipment Composition & Description | Process Flow and Utility Requirements | Remarks
1 | PECVD | 1.Robot | Description: The robot automatically loads pre-processed glass substrates into the load. Using the transfer system and associated equipment, the substrates are repositioned for subsequent processing. Afterward, the robot automatically transfers them to the flat conveyor for the next process stage. In addition, the PECVD exhaust gas treatment system (incinerator) is installed in the basement, where all process exhaust gases are treated. The gases are then conveyed through ductwork to an external exhaust abatement system for secondary treatment, and finally discharged to the atmosphere through the exhaust stack. | Utility Requirements: Electrical power, bulk gases, and specialty gases, including PH2, SiH4, PH3, B2H6, NF3, B2H6/H2, CH4, H2, and VMB, as well as CDA (Compressed Dry Air). All piping routes pass through the PECVD basement, while the distribution of specialty gases is managed via dedicated gas cabinets installed within the PECVD workshop.
2.Load
3.Sputtering Chambers ×7 Units
4.Return Conveyor ×2 Units
5.Train” Transfer System (incl. 5 Heating Furnaces, 2 Cooling Furnaces, 2 Transfer Aisles)
6.Cross-transfer Table (incl. 2 Buffer Tables, 1 Loading Table, 1 Cleaning Table, 2 Buffer Tables)
2

## DI Water Treatment Process Desc
Process Flow Diagram of RO (Reverse Osmosis) + EDI Water Treatment System
from raw water feed |  | Raw Water Tank | Raw Water Pump |  | Multimedia Filter (Quartz Sand) | Activated Carbon Filter (Pretreatment) | Water Softener
|  |  | Provides required working pressure for pretreatment units |  | Removes suspended solids, rust, etc. in raw water; adsorbs organics and residual chlorin |  | Removes hardness (Ca²⁺ and Mg²⁺)
RO concentrate is recycled back to the raw water tank for reprocessing
|  | Intermediate (Break) Tank | First-Pass, Two-Stage RO |  | RO High-Pressure Pump | Booster pump | Softened Water Tank
|  |  | Removes dissolved salts from water |  | The high-pressure pump provides the operating pressure required by the RO system to achieve the designed permeate flow and water quality. After pressurization, the filtered water reaches approximately 10 bar, ensuring sufficient feed pressure to the RO membranes and thereby maintaining the specified permeate production.
|  | Cartridge Filter | UV Sterilizer |  | EDI System (Electrodeionization) | Ultrapure Water Tank | Booster Pump
|  | Removes suspended particles of various sizes | Used for TOC removal, disinfection, and reduction of ozone/oxygen residuals |  | EDI applies an electric field to drive ion migration; ions are removed via ion-exchange membranes and resin. Product water resistivity > 15 MΩ·cm
Portion of the product water supplied for use
|  |  |  | Concentrate: Part of the concentrate from 1st & 2nd pass RO is recycled to the raw water tank, and the remainder is discharged to the municipal wastewater system |  |  | DI Water End-User Equipment