## Chemical Water System Sizing
Chemical Water System Calculation Sheet
I |  | System Design
1. | EDI (Electrodeionization) System | Required demineralized water flow (system requirement) |  | 10800 | m3/day
|  |  | or | 450 | m3/hr
|  | EDI design permeate (product) flow |  | 10800 | m3/day
|  |  | or | 450 | m3/hr
|  | EDI recovery |  | 90 | %
|  | EDI feed flow |  | 12000 | m3/day
|  |  |  | 500 | m3/hr
2. | Second-Pass Reverse Osmosis (RO-2) System | RO design permeate flow |  | 12000 | m3/day
|  |  | or | 500 | m3/hr
|  | RO design recovery |  | 90 | %
|  | RO design feed flow |  | 555.5556 | m3/hr
3. | First-Pass Reverse Osmosis (RO-1) System | RO design permeate flow |  | 11040 | m3/day
|  |  | or | 460 | m3/hr
|  | RO design recovery |  | 75 | %
|  | RO design feed flow |  | 613.3333 | m3/hr
4. | Concentrate/Brine RO System | RO design permeate flow |  | 2620.8 | m3/day
|  |  | or | 109.2 | m3/hr
|  | RO design recovery |  | 70 | %
|  | RO design feed flow |  | 153.3333 | m3/hr
|  | RO actual design feed flow |  | 156 | m3/hr
5. | Ultrafiltration (UF) System | UF design permeate flow |  | 17280 | m3/day
|  |  | or | 720 | m3/hr
|  | UF design recovery |  | 90 | %
|  | UF feed flow |  | 800 | m3/hr
|  | Total UF system feed flow |  | 800 | m3/hr
|  |  | or | 19200 | m3/day
|  | UF system water recovery |  | 90 | %
6. | Pretreatment System | Disc filter design recovery |  | 100 | % | Raw-water Backwash
|  | Disc filter design product flow |  | 800 | m3/hr
|  | Disc filter feed flow |  | 800 | m3/hr
|  | Disc filter actual feed flow |  | 800 | m3/hr
|  | Number of disc filters |  | 2 | units
|  | Per-unit filter product flow |  | 400 | m3/hr
|  | Per-unit filter actual design product flow |  | 400 | m3/hr
|  | Design water temperature |  | 25 | ℃
II |  | Process Water Pretreatment System Design
1. |  | Raw Water Tank |  |  |  | recommand of suggestion
| Requirements | Inlet residence time |  | 2 | hr
| Process Calculations | Inlet flow rate |  | 800 | m3/hr
|  | Theoretical storage capacity |  | 1600 | m3
|  | Safety margin |  | 20 | %
|  | Required storage capacity |  | 1920 | m3
|  | Design storage capacity |  | 2000 | m3
|  | Design quantity |  | 2 | units
|  | Storage capacity per tank |  | 1000 | m3
| Selection | Actual capacity per tank |  | 1000 | m3
|  | Actual quantity provided |  | 2 | units
2. |  | Raw Water Pump
| Requirements | Required capacity (flow) |  | 800 | m3/hr
|  | Required head |  | 40 | m
| Process Calculations | Design capacity |  | 800 | m3/hr
|  | Number of operating pumps |  | 2 | units
|  | Single-pump capacity |  | 400 | m3/hr
|  | Design single-pump capacity |  | 400 | m3/hr
|  | Design single-pump head |  | 40 | m
| Selection | Flow per pump |  | 400 | m3/hr
|  | Head per pump |  | 40 | m
|  | Actual quantity provided |  | 3 | units | 2 in operation，1 standby
3. |  | Sodium Hypochlorite Dosing System
| Requirements | NaClO dosage concentration (as available chlorine) |  | 2 | mg/L
38
| Process Calculations | NaClO dosing rate |  | 1.6 | kg/hr | Neat Chemical (100% active)
|  |  | or | 38.4 | kg/d
|  | NaClO solution concentration |  | 10 | % | Commercial Solution Concentration
|  | NaClO solution consumption |  | 16 | L/hr
|  |  | or | 384 | L/day
|  | Metering pump operating flow |  | 16 | L/hr
|  | Metering pump operating duty |  | 50 | %
|  | Calculated capacity of metering pump |  | 32 | L/hr
|  | Number of metering pumps in operation |  | 1 | unit
|  | Per-pump capacity |  | 32 | L/hr
| Selection | Actual metering pump capacity |  | 38 | L/hr
|  | Metering pump discharge head |  | 5.5 | bar
|  | Actual number of pumps |  | 2 | units | 1 in operation，1 standby
Dosing Tank
| Process Calculations | Chemical storage time in dosing tank |  | 1 | day
|  | Dosing tank storage capacity |  | 384 | L
|  | Actual storage capacity per tank |  | 500 | L
|  | Number of tanks in operation |  | 1 | unit
| Selection | Storage capacity per tank |  | 500 | L
|  | Actual quantity provided |  | 1 | unit | 1 in operation，1 standby
4. |  | Coagulant Dosing System
| Requirements | Coagulant dosage concentration |  | 2 | mg/L
38
| Process Calculations | Coagulant Dosage |  | 1.6 | kg/hr | Neat Chemical (100% active)
|  |  | or | 38.4 | kg/d
|  | Coagulant Solution Concentration |  | 10 | % | Commercial Solution Concentration
|  | Coagulant Solution Consumption |  | 16 | L/hr
|  |  | or | 384 | L/day
|  | Metering Pump Operating Flow Rate |  | 16 | L/hr
|  | Metering Pump Operating Load |  | 50 | %
|  | Calculated Pump Capacity |  | 32 | L/hr
|  | Number of Pumps in Operation |  | 1 | unit
|  | Rated Pump Capacity per Unit |  | 32 | L/hr
| Selection | Actual Pump Capacity |  | 38 | L/hr
|  | Pump Head per Unit |  | 5.5 | bar
|  | Actual Number of Pumps |  | 2 | units | 1 in operation，1 standby
| Process Calculations | Chemical Tank Retention Time |  | 1 | day
|  | Chemical Tank Storage Capacity |  | 384 | L
|  | Actual Storage Capacity per Tank |  | 500 | L
|  | Number of Tanks in Operation |  | 1 | unit
| Selection | Design Storage Capacity per Tank |  | 500 | L
|  | Actual Number of TanksTank |  | 1 | unit | 1 in operation，1 standby
5. |  | Non-oxidizing Biocide
| Requirements | Biocide Dosage Concentration |  | 2 | mg/L
38
| Process Calculations | Biocide Dosage |  | 1.6 | kg/hr | Neat Chemical (100% active)
|  |  | or | 38.4 | kg/d
|  | Biocide Solution Concentration |  | 10 | % | Commercial Solution Concentration
|  | Biocide Solution Consumption |  | 16 | L/hr
|  |  | or | 384 | L/day
|  | Metering Pump Operating Flow Rate |  | 16 | L/hr
|  | Metering Pump Operating Load |  | 50 | %
|  | Calculated Pump Capacity |  | 32 | L/hr
|  | Number of Pumps in Operation |  | 1 | unit
|  | Rated Pump Capacity per Unit |  | 32 | L/hr
| Selection | Actual Pump Capacity |  | 38 | L/hr
|  | Pump Head per Unit |  | 5.5 | bar
|  | Actual Number of Pumps |  | 2 | units | 1 in operation，1 standby
| Process Calculations | Chemical Tank Retention Time |  | 1 | day
|  | Chemical Tank Storage Capacity |  | 384 | L
|  | Actual Storage Capacity per Tank |  | 500 | L
|  | Number of Tanks in Operation |  | 1 | unit
| Selection | Design Storage Capacity per Tank |  | 500 | L
|  | Actual Number of TanksTank |  | 1 | unit | 1 in operation，1 standby
6. |  | Sodium Bisulfite Dosing System
| Requirements | NaHSO₃ Dosage Concentration |  | 2 | mg/L
| Process Calculations | NaHSO₃ Dosage |  | 1.44 | kg/hr | Neat Chemical (100% active)
|  |  | or | 34.56 | kg/day
|  | NaHSO₃ Solution Concentration |  | 10 | % | Prepared Solution Concentration (solid dissolution)
|  | NaHSO₃ Solution Consumption |  | 14.4 | L/hr
|  |  | or | 345.6 | L/day
|  | Metering Pump Operating Flow Rate |  | 14.4 | L/hr
|  | Metering Pump Operating Load |  | 50 | %
|  | Calculated Pump Capacity |  | 28.8 | L/hr
|  | Number of Pumps in Operation |  | 1 | unit
|  | Capacity per dosing pump |  | 28.8 | L/hr
| Selection | Actual Pump Capacity |  | 38 | L/hr
|  | Pump Head per Unit |  | 5.5 | bar
|  | Actual Number of Pumps |  | 2 | units | 1 in operation，1 standby
| Process Calculations | Chemical Tank Retention Time |  | 1 | day
|  | Chemical Tank Storage Capacity |  | 345.6 | L
|  | Actual storage capacity of dosing tank |  | 500 | L
|  | Number of Tanks in Operation |  | 1 | unit
|  | Design Storage Capacity per Tank |  | 500 | L
| Selection | Design Storage Capacity per Tank |  | 500 | L
|  | Actual Number of TanksTank |  | 2 | units | 1 Mixing Tank，1 Dosing Tank
7. |  | Heat Exchanger
| Requirements | Heat Exchangerdesign inlet water flow rate |  | 800 | m3/hr
|  | Number of plate heat exchangers |  | 2 | units
|  | Inlet water flow per unit plate heat exchanger |  | 400 | m3/hr | Temperature raised from 5 °C to 25 °C
|  | Steam flow per unit plate heat exchanger |  | 29.3 | t/h | Main Header DN350, Branch DN250
8. |  | UF Backwash Chemical Dosing System (NaClO / HCl / NaOH)
| Selection | NaClO dosage concentration |  | 192 | mg/L
| Process Calculations | NaClO dosage |  | 24.96 | kg/hr | Neat Chemical (100% active)
|  |  | or | 599.04 | kg/d
|  | NaClO solution concentration |  | 10 | % | Commercial Solution Concentration
|  | NaClO solution consumption |  | 249.6 | L/hr
|  |  | or | 5990.4 | L/day
|  | Metering Pump Operating Flow Rate |  | 249.6 | L/hr
|  | Metering Pump Operating Load |  | 50 | %
|  | Calculated Pump Capacity |  | 499.2 | L/hr
|  | Number of Pumps in Operation |  | 1 | unit
|  | Rated Pump Capacity per Unit |  | 499.2 | L/hr
| Selection | Actual Pump Capacity |  | 500 | L/hr
|  | Pump Head per Unit |  | 5 | bar
|  | Actual Number of Pumps |  | 3 | units | 2 in operation，1 standby，1 UF backwash unit for reuse-water system
| Process Calculations | Chemical Tank Retention Time |  | 3 | day
|  | Chemical Tank Storage Capacity |  | 561.6 | L
|  | Actual Storage Capacity per Tank |  | 1000 | L
|  | Number of Tanks in Operation |  | 1 | unit
| Selection | Design Storage Capacity per Tank |  | 1000 | L
|  | Actual Number of TanksTank |  | 2 | units | 1 in operation，1 standby/shared with reuse-water UF
9. |  | Disc Filter
| Requirements | Design filtrate flow rate of disc filter |  | 19200 | m3/day
|  |  | or | 800 | m3/hr
|  | Actual design filtrate flow of disc filter |  | 800
|  | Number of units in operation |  | 2 | units
|  | Flow rate per unit |  | 400 | m3/hr
III |  | Chemical Water UF System Design
|  | UF feedwater flow rate | 800 | m3/h
|  | Number of operating UF units | 4 | trains
|  | Feedwater flow per UF unit | 200
|  | UF recovery rate | 90 | %
|  | Total UF permeate flow | 720 | m3/h
|  | Permeate flow per UF unit | 180 | m3/h
|  | UF membrane flux | 60 | L/H.m2
|  | UF membrane area | 80 | m2
|  | Number of UF elements per train | 37.5 | elements
|  | Actual number of UF elements per train | 42 | elements |  | Per Vendor Design Calculation
UF Permeate Tank
| Requirements | Hydraulic retention time | 0.35 | hr
| Process Calculations | Inlet flow rate | 720 | m3/hr
|  | Theoretical storage capacity | 302.4 | m3
|  | Safety margin | 20 | %
|  | Required storage capacity | 362.88 | m3
|  | Design storage capacity | 400 | m3
|  | Number of designed tanks | 1 | unit
|  | Storage capacity per tank | 400 | m3
| Selection | Actual storage capacity per tank | 400 | m3
|  | Actual number of tanks | 1 | unit
1st-pass RO Feedwater Pump
|  | Design flow rate | 613 | m3/h
|  | Actual flow rate | 306.5 | m3/h |  | 310
|  | Pump head | 30 | m
|  | Number of pumps | 2 | units
|  | Actual number of tanks | 3 | units | 2 in operation，1 standby
UF Backwash Pump
|  | Design flow rate | 400 | m3/h |  | Tentative – subject to vendor calculation
|  | Actual flow rate | 400 | m3/h
|  | Pump head | 20 | m
|  | Number of pumps | 1 | unit | 1 in operation，1 standby | VFD Control
IV |  | 1st-pass RO System Design
1. |  | 1st-pass RO Antiscalant Dosing System
| Requirements | Antiscalant dosage concentration |  | 3 | mg/L
| Process Calculations | Antiscalant dosage |  | 2.16 | kg/hr | Neat Chemical (100% active)
|  |  | or | 51.84 | kg/day
|  | Antiscalant solution concentration |  | 10 | % | Diluted Solution Concentrration
|  | Antiscalant solution consumption |  | 21.6 | L/hr
|  |  | or | 518.4 | L/day
|  | Metering Pump Operating Flow Rate |  | 21.6 | L/hr
|  | Metering Pump Operating Load |  | 50 | %
|  | Calculated Pump Capacity |  | 43.2 | L/hr
|  | Number of Pumps in Operation |  | 4 | units
|  | Capacity per dosing pump |  | 10.8 | L/hr
| Selection | Actual Pump Capacity |  | 15.1 | L/hr
|  | Pump Head per Unit |  | 5 | bar
|  | Actual Number of Pumps |  | 5 | units | 4 duty，1 standby
| Process Calculations | Chemical Tank Retention Time |  | 1 | day
|  | Chemical Tank Storage Capacity |  | 518.4 | L
|  | Actual storage capacity of dosing tank |  | 500 | L
|  | Number of Tanks in Operation |  | 1 | unit
|  | Design Storage Capacity per Tank |  | 500 | L
| Selection | Design Storage Capacity per Tank |  | 500 | L
|  | Actual Number of TanksTank |  | 1 | unit | 1 in operation，0standbyl
2. |  | 1st-pass RO Cartridge Filter
| Requirements | Required cartridge filter capacity |  | 613.3333 | m3/hr
| Process Calculations | Design capacity |  | 613.3333 | m3/hr
|  | Number of units in operation |  | 4 | units
|  | Design capacity per filter unit |  | 153.3333 | m3/hr
| Selection | Filter unit capacity |  | 155 | m3/hr | 4 High-Flow Cartridges, DN450, Vertical
|  | Cartridge FilterActual number of tanks |  | 4 | units | 4 in operation，0 standby
|  | Filtration rating |  | 5 | μm
3. |  | 1st-pass RO High Pressure Pump
| Requirements | Required capacity |  | 613.3333 | m3/hr
|  | Required Pump head |  | 120 | m | Refer to RO Design Calculation
| Process Calculations | Design capacity |  | 613.3333 | m3/hr
|  | operating Number of pumps |  | 4 | units
|  | Design capacity per pump |  | 153.3333 | m3/hr
|  | Design pump head per pump |  | 120 | m
| Selection | Flow rate per pump |  | 155 | m3/hr
|  | Pump head per pump |  | 120 | m
|  | Actual number of tanks |  | 4 | units | 4 in operation，0 standby
4 |  | 1st-pass RO Unit
| Requirements | RO membrane supplier |  | DuPont FilmTec™
|  |  | or | Hydranautics™
|  |  | or | Toray™
|  | RO array configuration |  | First-Pass, Two-Stage Configuration
|  | Average permeate flux (as per supplier’s design guidelines) |  | 22~29 | lmh
|  | Water recovery rate |  | 75 | %
|  | Feedwater temperature |  | 25 | ℃
| Process Calculations | Single RO Train |  |  |  | Refer to RO Design Calculation
| Selection | First-stage RO sectio
|  | Number of pressure vessels pumps (1st stage) |  | 13 | elements
|  | Number of elements per vessel pumps |  | 6 | elements
|  | Total number of RO elements pumps |  | 78 | elements | Total number of RO elements pumps
Membrane selection
or
Second-stage RO section
|  | Number of pressure vessels pumps (2nd stage) |  | 6 | elements
|  | Number of elements per vessel pumps |  | 6 | elements
|  | Total number of RO elements pumps |  | 36 | elements
Membrane selection
|  |  | or | BW30-400
| operating参数 | Average permeate flux (1nd stage) |  | 29.09 | lmh
|  | Average permeate flux (2nd stage) |  | 22.92 | lmh
|  | Average permeate flux |  | 27.14 | lmh
|  | Inlet flow rate per pressure vessel (1st stage） |  | 11.7946 | m3/hr
|  | Feed pressure (1st stage) |  | 11.19 | bar
|  | Permeate flow (1st stage) |  | 84.33 | m3/hr
|  | Inlet flow rate per pressure vessel (1st stage) |  | 5.3077 | m3/hr
|  | Inlet flow rate per pressure vessel (2nd stage) |  | 11.5 | m3/hr
|  | Feed pressure (2nd stage) |  | 9.17 | bar
|  | Permeate flow (2nd stage) |  | 30.66 | m3/hr
|  | Brine flow rate per vessel (2nd stage) |  | 6.3917 | m3/hr
|  | Brine flow rate |  | 38.35 | m3/hr
|  | RO permeate flow |  | 115 | m3/hr
|  | Number of 1st-pass RO pumps |  | 4 | trains
|  | Total permeate flow of 1st-pass RO |  | 460
|  | Total brine flow rate of 1st-pass RO |  | 153.4
5. |  | 1st-pass RO Permeate Tank |  |  |  | Recommendation(s) / Notes
| Requirements | Hydraulic retention time |  | 0.3 | hr
| Process Calculations | Inlet flow rate |  | 460 | m3/hr
|  | Theoretical storage capacity |  | 138 | m3
|  | Safety margin |  | 20 | %
|  | Required storage capacity |  | 172.5 | m3
|  | Design storage capacity |  | 200 | m3
|  | Number of designed tanks |  | 1 | unit
|  | Storage capacity per tank |  | 200 | m3
| Selection | Actual storage capacity per tank |  | 200 | m3
|  | Actual number of tanks |  | 1 | unit
6. |  | RO Flushing Pump
| Requirements | Maximum flushing water per pressure vessel |  | 10.2 | m3/hr
|  | Required flushing pressure |  | 1.5~4.0 | bar
| Process Calculations | Number of pressure vessels in 2nd-stage RO section |  | 6
|  | Required flow rate of a single RO train |  | 61.2 | m3/hr
|  | operatingNumber of pumps |  | 1 | unit
|  | capacity per pump |  | 61.2 | m3/hr
|  | Design capacity per pump |  | 61.2 | m3/hr
|  | Design pump head per pump |  | 30 | m
| Selection | Flow rate per pump |  | 55 | m3/hr
|  | Pump head per pump |  | 35 | m
|  | Actual number of tanks |  | 1 | unit | 1 in operation，1 standby
7. |  | RO Cleaning Tank
| Requirements | Cleaning solution per membrane element |  | 55 | L
| Process Calculations | Cleaning solution per 1st-stage element |  | 4.29 | m3
|  | Piping volume |  | 0.7065 | m3
|  | Required capacity |  | 4.9965 | m3
|  | Safety margin |  | 10 | %
|  | Design storage capacity |  | 5.5517 | m3
| Selection | Actual capacity |  | 6 | m3
|  | Actual number of tanks |  | 1 | unit | 1 in operation，0standby
8. |  | RO Cleaning Pump
| Requirements | Inlet flow rate for cleaning of a single pressure vessel |  | 8.5 | m3/hr | Design Guideline: 8–10.2 m³/h
| Process Design | 1st-stage pressure vessel pumps |  | 13 | elements
|  | Cleaning flow rate per single RO train |  | 110.5 | m3/hr
|  | operatingNumber of pumps |  | 1 | unit
|  | capacity per pump |  | 110.5 | m3/hr
|  | Design pump head per pump |  | 30 | m
| Selection | Flow rate per pump |  | 110 | m3/hr
|  | Pump head per pump |  | 35 | m
|  | Actual number of tanks |  | 1 | unit | 1 in operation，0standby
9. |  | RO Cleaning Cartridge Filter
| Requirements | Required cartridge filter capacity |  | 110 | m3/hr | 3 Cartridges, DN400, Vertical
| Process Calculations | Design capacity |  | 110 | m3/hr
|  | Number of units in operation |  | 1 | unit
|  | Design capacity per filter unit |  | 110 | m3/hr
| Selection | Filter unit capacity |  | 110 | m3/hr
|  | Cartridge FilterActual number of tanks |  | 1 | unit | 1 in operation，0standby
|  | Filtration rating |  | 5 | μm
10. |  | 1st-pass RO Brine Tank |  |  |  | Recommendation(s) / Notes
| Requirements | Hydraulic retention time |  | 1.5 | hr
| Process Calculations | Inlet flow rate |  | 153.4 | m3/hr
|  | Theoretical storage capacity |  | 230.1 | m3
|  | Safety margin |  | 20 | %
|  | Required storage capacity |  | 287.625 | m3
|  | Design storage capacity |  | 400 | m3
|  | Number of designed tanks |  | 1 | unit
|  | Storage capacity per tank |  | 400 | m3
| Selection | Actual storage capacity per tank |  | 400 | m3
|  | Actual number of tanks |  | 1 | unit
11. |  | Brine RO Booster Pum
| Requirements | Required capacity |  | 153.4 | m3/hr
|  | Required Pump head |  | 30 | m | Refer to RO Design Calculation
| Process Calculations | Design capacity |  | 153.4 | m3/hr
|  | operatingNumber of pumps |  | 1 | unit
|  | Design capacity per pump |  | 153.4 | m3/hr
|  | Design pump head per pump |  | 30 | m
| Selection | Flow rate per pump |  | 160 | m3/hr
|  | Pump head per pump |  | 30 | m
|  | Actual number of tanks |  | 2 | units | 1 in operation，1 standby
V |  | Brine RO System Design
1. |  | Brine RO Acid Dosing System
| Requirements | HCl dosage concentration |  | 100 | mg/L
| Process Calculations | HCl dosage |  | 15.34 | kg/hr | Neat Chemical (100% active)
|  |  | or | 368.16 | kg/day
|  | HCl solution concentration |  | 31 | % | Diluted Solution Concentrration
|  | HCl solution consumption |  | 49.4839 | L/hr
|  |  | or | 1187.6129 | L/day
|  | Metering Pump Operating Flow Rate |  | 49.4839 | L/hr
|  | Metering Pump Operating Load |  | 50 | %
|  | Calculated Pump Capacity |  | 98.9677 | L/hr
|  | Number of Pumps in Operation |  | 1 | unit
|  | Capacity per dosing pump |  | 98.9677 | L/hr
| Selection | Actual Pump Capacity |  | 120 | L/hr
|  | Pump Head per Unit |  | 5 | bar
|  | Actual Number of Pumps |  | 2 | units | 1 in operation，1 standby, automatic control
| Process Calculations | Chemical Tank Retention Time |  | 1 | day
|  | Actual storage capacity of dosing tank |  | 1187.6129 | L
|  | Number of Tanks in Operation |  | 1 | unit
|  | Design Storage Capacity per Tank |  | 1187.6129 | L
| Selection | Design Storage Capacity per Tank |  | 500 | L
|  | Actual Number of TanksTank |  | 1 | unit | 1 in operation，0standbyl
2. |  | Brine RO Antiscalant Dosing System
| Requirements | Antiscalant dosage concentration |  | 5 | mg/L
| Process Calculations | Antiscalant dosage |  | 0.767 | kg/hr | Neat Chemical (100% active)
|  |  | or | 18.408 | kg/day
|  | Antiscalant solution concentration |  | 10 | % | Diluted Solution Concentrration
|  | Antiscalant solution consumption |  | 7.67 | L/hr
|  |  | or | 184.08 | L/day
|  | Metering Pump Operating Flow Rate |  | 7.67 | L/hr
|  | Metering Pump Operating Load |  | 50 | %
|  | Calculated Pump Capacity |  | 15.34 | L/hr
|  | Number of Pumps in Operation |  | 1 | unit
|  | Capacity per dosing pump |  | 15.34 | L/hr
| Selection | Actual Pump Capacity |  | 30.3 | L/hr
|  | Pump Head per Unit |  | 4.1 | bar
|  | Actual Number of Pumps |  | 2 | units | 1 in operation，1 standby
| Process Calculations | Chemical Tank Retention Time |  | 1 | day
|  | Actual storage capacity of dosing tank |  | 184.08 | L
|  | Number of Tanks in Operation |  | 1 | unit
|  | Design Storage Capacity per Tank |  | 184.08 | L
| Selection | Design Storage Capacity per Tank |  | 500 | L
|  | Actual Number of TanksTank |  | 1 | unit | 1 in operation，0standbyl
2. |  | Brine RO Cartridge Filter
| Requirements | Required cartridge filter capacity |  | 153.4 | m3/hr
| Process Calculations | Design capacity |  | 153.4 | m3/hr
|  | Number of units in operation |  | 1 | unit
|  | Design capacity per filter unit |  | 153.4 | m3/hr
| Selection | Filter unit capacity |  | 160 | m3/hr | 4 High-Flow Cartridges, DN450, Vertical
|  | Cartridge FilterActual number of tanks |  | 1 | unit | 1 in operation，0standby
|  | Filtration rating |  | 5 | μm
3. |  | Brine RO High Pressure Pump
| Requirements | Required capacity |  | 153.4 | m3/hr
|  | Required Pump head |  | 125 | m | Refer to RO Design Calculation
| Process Calculations | Design capacity |  | 153.4 | m3/hr
|  | operatingNumber of pumps |  | 1 | unit
|  | Design capacity per pump |  | 153.4 | m3/hr
|  | Design pump head per pump |  | 130 | m
| Selection | Flow rate per pump |  | 160 | m3/hr
|  | Pump head per pump |  | 150 | m
|  | Actual number of tanks |  | 1 | unit | 1 in operation，0standby
4 |  | Brine RO Unit
| Requirements | RO membrane supplier |  | DuPont FilmTec™
|  |  | or | Hydranautics™
|  |  | or | Toray™
|  | RO array configuration |  | First-Pass, Two-Stage Configuration
|  | Average permeate flux (as per supplier’s design guidelines) |  | 27~32 | lmh
|  | Water recovery rate |  | 70 | %
|  | Feedwater temperature |  | 25 | ℃
| Process Design | Single RO Train |  |  |  | Refer to RO Design Calculation
| Selection | First-stage RO sectio
|  | Number of pressure vessels pumps (1st stage) |  | 11 | elements
|  | Number of elements per vessel pumps |  | 6 | elements
|  | Total number of RO elements pumps |  | 66 | elements
Membrane selection
or
Second-stage RO section
|  | Number of pressure vessels pumps (2nd stage) |  | 6 | elements
|  | Number of elements per vessel pumps |  | 6 | elements
|  | Total number of RO elements pumps |  | 36 | elements
Membrane selection
|  |  | or | BW30-400
| operating参数 | Average permeate flux (1nd stage) |  | 29.37 | lmh
|  | Average permeate flux (2nd stage) |  | 23.05 | lmh
|  | Average permeate flux |  | 27.16 | lmh
|  | Inlet flow rate per pressure vessel (1st stage） |  | 13.3 | m3/hr
|  | Feed pressure (1st stage) |  | 12.07 | bar
|  | Permeate flow (1st stage) |  | 85.12 | m3/hr
|  | Inlet flow rate per pressure vessel (1st stage) |  | 6.76 | m3/hr
|  | Inlet flow rate per pressure vessel (2nd stage) |  | 12.55 | m3/hr
|  | Feed pressure (2nd stage) |  | 11.85 | bar
|  | Permeate flow (2nd stage) |  | 35.98 | m3/hr
|  | Brine flow rate per vessel (2nd stage) |  | 7.41 | m3/hr
|  | Brine flow rate |  | 51.9 | m3/hr
|  | RO permeate flow |  | 109 | m3/hr
|  | Number of 1st-pass RO pumps |  | 1 | train
|  | Total permeate flow of 1st-pass RO |  | 109
5. |  | Brine RO Flushing Pump
| Requirements | Maximum flushing water per pressure vessel |  | 10.2 | m3/hr
|  | Required flushing pressure |  | 1.5~4.0 | bar
| Process Calculations | Number of pressure vessels in 2nd-stage RO section |  | 6
|  | Required flow rate of a single RO train |  | 61.2 | m3/hr
|  | operatingNumber of pumps |  | 1 | unit
|  | capacity per pump |  | 61.2 | m3/hr
|  | Design capacity per pump |  | 61.2 | m3/hr
|  | Design pump head per pump |  | 30 | m
| Selection | Flow rate per pump |  | 60 | m3/hr
|  | Pump head per pump |  | 35 | m
|  | Actual number of tanks |  | 1 | unit | 1 in operation ，shares standby pump with 1st-Pass RO Flush Pump
6. |  | Brine RO Concentrate Tank |  |  |  | Recommendation(s) / Notes
| Requirements | Hydraulic retention time |  | 0.5 | hr
| Process Calculations | Inlet flow rate |  | 51.9 | m3/hr
|  | Theoretical storage capacity |  | 25.95 | m3
|  | Safety margin |  | 20 | %
|  | Required storage capacity |  | 32.4375 | m3
|  | Design storage capacity |  | 50 | m3
|  | Number of designed tanks |  | 1 | unit
|  | Storage capacity per tank |  | 50 | m3
| Selection | Actual storage capacity per tank |  | 50 | m3
|  | Actual number of tanks |  | 1 | unit
7. |  | Brine RO Concentrate Transfer Pump
| Selection | Flow rate per pump |  | 50 | m3/hr
|  | Pump head per pump |  | 35 | m
|  | Actual number of tanks |  | 2 | units | 1 in operation，1 standby
8. |  | Brine RO Cleaning Pump
| Requirements | Inlet flow rate for cleaning of a single pressure vessel |  | 8.5 | m3/hr | Design Guideline: 8–10.2 m³/h
| Process Design | 1st-stage pressure vessel pumps |  | 11 | elements
|  | Cleaning flow rate per single RO train |  | 93.5 | m3/hr
|  | operatingNumber of pumps |  | 1 | unit
|  | capacity per pump |  | 93.5 | m3/hr
|  | Design pump head per pump |  | 35 | m
| Selection | Flow rate per pump |  | 120 | m3/hr
|  | Pump head per pump |  | 35 | m
|  | Actual number of tanks |  | 1 | unit | Shared with 1st-Pass RO CIP Pump
VI |  | 2nd-pass RO System Design
1. |  | 2nd-pass RO Booster Pump
| Selection | Flow rate per pump |  | 280 | m3/hr
|  | Pump head per pump |  | 30 | m
|  | Actual number of tanks |  | 3 | units | 2 in operation，1 standby
2. |  | 2nd-pass RO pH Adjustment Dosing System
| Requirements | NaOH dosage concentration |  | 5 | mg/L
| Process Calculations | NaOH dosage |  | 2.8 | kg/hr | Neat Chemical (100% active)
|  |  | or | 67.2 | kg/day
|  | NaOH solution concentration |  | 31 | % | Diluted Solution Concentrration
|  | NaOH solution consumption |  | 9.0323 | L/hr
|  |  | or | 216.7742 | L/day
|  | Metering Pump Operating Flow Rate |  | 9.0323 | L/hr
|  | Metering Pump Operating Load |  | 50 | %
|  | Calculated Pump Capacity |  | 18.0645 | L/hr
|  | Number of Pumps in Operation |  | 1 | unit
|  | Capacity per dosing pump |  | 18.0645 | L/hr
| Selection | Actual Pump Capacity |  | 38 | L/hr
|  | Pump Head per Unit |  | 5 | bar
|  | Actual Number of Pumps |  | 2 | units | 1 in operation，1 standby
| Process Calculations | Chemical Tank Retention Time |  | 1 | day
|  | Actual storage capacity of dosing tank |  | 200 | L
|  | Number of Tanks in Operation |  | 1 | unit
|  | Design Storage Capacity per Tank |  | 200 | L
| Selection | Design Storage Capacity per Tank |  | 200 | L
|  | Actual Number of TanksTank |  | 1 | unit | 1 in operation，0standbyl
3. |  | 2nd-pass RO Cartridge Filter
| Requirements | Required cartridge filter capacity |  | 560 | m3/hr
| Process Calculations | Design capacity |  | 560 | m3/hr
|  | Number of units in operation |  | 4 | units
|  | Design capacity per filter unit |  | 140 | m3/hr
| Selection | Filter unit capacity |  | 140 | m3/hr | 3 Cartridges, DN400, Vertical
|  | Cartridge FilterActual number of tanks |  | 4 | units | 4 in operation，0 standby
|  | Filtration rating |  | 5 | μm
4. |  | 2nd-pass RO High Pressure Pump
| Requirements | Required capacity |  | 140 | m3/hr
|  | Required Pump head |  | 140 | m | Refer to RO Design Calculation
| Process Calculations | Design capacity |  | 140 | m3/hr
|  | operatingNumber of pumps |  | 4 | units
|  | Design capacity per pump |  | 35 | m3/hr
|  | Design pump head per pump |  | 140 | m
| Selection | Flow rate per pump |  | 140 | m3/hr
|  | Pump head per pump |  | 140 | m
|  | Actual number of tanks |  | 4 | units | 4 in operation，0 standby
5. |  | 2nd-pass RO High Pressure Pump
| Requirements | RO membrane supplier |  | DuPont FilmTec™
|  |  | or | Hydranautics™
|  |  | or | Toray™
|  | RO array configuration |  | First-Pass, Two-Stage Configuration
|  | Average permeate flux (as per supplier’s design guidelines) |  | 36~43 | lmh
|  | Water recovery rate |  | 75 | %
|  | Feedwater temperature |  | 20 | ℃
| Process Design | Single RO Train |  |  |  | Refer to RO Design Calculation
| Selection | First-stage RO sectio
|  | Number of pressure vessels pumps (1st stage) |  | 11 | elements
|  | Number of elements per vessel pumps |  | 6 | elements
|  | Total number of RO elements pumps |  | 66 | elements
|  | Membrane selection |  |  |  | Fouling-Resistant Type
|  |  | or |  |  | Fouling-Resistant Type
Second-stage RO section
|  | Number of pressure vessels pumps (2nd stage) |  | 6 | elements
|  | Number of elements per vessel pumps |  | 6 | elements
|  | Total number of RO elements pumps |  | 36 | elements
Membrane selection
|  |  | or | BW30-400
| operating参数 | Average permeate flux (1nd stage) |  | 34.53 | lmh
|  | Average permeate flux (2nd stage) |  | 30.15 | lmh
|  | Average permeate flux |  | 32.98 | lmh
|  | Inlet flow rate per pressure vessel (1st stage） |  | 14.2 | m3/hr
|  | Feed pressure (1st stage) |  | 13.31 | bar
|  | Permeate flow (1st stage) |  | 84.69 | m3/hr
|  | Inlet flow rate per pressure vessel (1st stage) |  | 6.5 | m3/hr
|  | Inlet flow rate per pressure vessel (2nd stage) |  | 11.92 | m3/hr
|  | Feed pressure (2nd stage) |  | 10.78 | bar
|  | Permeate flow (2nd stage) |  | 40.33 | m3/hr
|  | Brine flow rate per vessel (2nd stage) |  | 15.615 | m3/hr
|  | Brine flow rate |  | 31.23 | m3/hr
|  | RO permeate flow |  | 125 | m3/hr
|  | Number of 2nd-pass RO pumps |  | 4 | trains
|  | Total permeate flow rate of 2nd-pass RO |  | 500
6. |  | 2nd-pass RO Permeate Tank |  |  |  | Recommendation(s) / Notes
| Requirements | Hydraulic retention time |  | 0.3 | hr
| Process Calculations | Inlet flow rate |  | 500 | m3/hr
|  | Theoretical storage capacity |  | 150 | m3
|  | Safety margin |  | 20 | %
|  | Required storage capacity |  | 187.5 | m3
|  | Design storage capacity |  | 200 | m3
|  | Number of designed tanks |  | 1 | unit
|  | Storage capacity per tank |  | 200 | m3
| Selection | Actual storage capacity per tank |  | 200 | m3
|  | Actual number of tanks |  | 1 | unit
7. |  | EDI Booster Pump
| Requirements | Required capacity |  | 500 | m3/hr
|  | Required Pump head |  | 50 | m | Refer to RO Design Calculation
| Process Calculations | Design capacity |  | 500 | m3/hr
|  | operatingNumber of pumps |  | 4 | units
|  | Design capacity per pump |  | 125 | m3/hr
|  | Design pump head per pump |  | 50 | m
| Selection | Flow rate per pump |  | 160 | m3/hr
|  | Pump head per pump |  | 50 | m
|  | Actual number of tanks |  | 4 | units | 4 in operation，0 standby
8. |  | EDICartridge Filter
| Requirements | Required cartridge filter capacity |  | 500 | m3/hr
| Process Calculations | Design capacity |  | 500 | m3/hr
|  | Number of units in operation |  | 4 | units
|  | Design capacity per filter unit |  | 125 | m3/hr
| Selection | Filter unit capacity |  | 125 | m3/hr | 3 Cartridges, DN400, Vertical
|  | Cartridge FilterActual number of tanks |  | 4 | units | 4 in operation，0 standby
|  | Filtration rating |  | 1 | μm
9. |  | Number of 2st-pass RO Cleaning Pump
| Requirements | Inlet flow rate for cleaning of a single pressure vessel |  | 8.5 | m3/hr | Design Guideline: 8–10.2 m³/h
| Process Design | 1st-stage pressure vessel pumps |  | 11 | elements
|  | Cleaning flow rate per single RO train |  | 93.5 | m3/hr
|  | operatingNumber of pumps |  | 1 | unit
|  | capacity per pump |  | 93.5 | m3/hr
|  | Design pump head per pump |  | 35 | m
| Selection | Flow rate per pump |  | 120 | m3/hr
|  | Pump head per pump |  | 35 | m
|  | Actual number of tanks |  | 1 | unit | Shared with 1st-Pass RO CIP Pump
VII |  | EDI System
1 |  | EDI SystemInlet flow rate | 500 | m3/h
|  | EDI product water flow rate | 450 | m3/h
|  | Number of operating UF units | 4 | trains
|  | Product water flow rate per EDI unit | 112.5
|  | UF recovery rate | 90 | %
|  | Number of EDI modules per train | 15 | pieces
|  | Number of stacks per train | 3 | sets
|  | Total number of modules Total number of pumps | 60 | pieces
EDI cleaning system shared with RO
2. |  | Demineralized Water Tank (V72001) |  |  |  | Recommendation(s) / Notes
| Requirements | Hydraulic retention time |  | 1.5 | hr
| Process Calculations | Inlet flow rate |  | 450 | m3/hr
|  | Theoretical storage capacity |  | 675 | m3
|  | Regeneration water volume |  | 57.6 | m3
|  | Safety margin |  | 20 | %
|  | Required storage capacity |  | 915.75 | m3
|  | Design storage capacity |  | 1000 | m3
|  | operatingNumber of pumps |  | 1 | unit
|  | Storage capacity per tank |  | 1000 | m3
| Selection | Actual storage capacity per tank |  | 1000 | m3
|  | Actual number of tanks |  | 2 | units
3. |  | Demineralized Water Pump (P72001)
| Requirements | Required capacity |  | 690 | m3/hr
|  | Required Pump head |  | 120 | m
| Process Calculations | Design capacity |  | 690 | m3/hr
|  | operatingNumber of pumps |  | 2 | units
|  | Design capacity per pump |  | 345 | m3/hr
|  | Design pump head per pump |  | 120 | m
| Selection | Flow rate per pump |  | 345 | m3/hr
|  | Pump head per pump |  | 120 | m
|  | Actual number of tanks |  | 3 | units | 2 in operation，1 standby
4. |  | Ammonia Dosing System
| Requirements | Ammonia dosage concentration |  | 1.5 | mg/L
38
| Process Calculations | Ammonia solution dosage |  | 1.035 | kg/hr | Neat Chemical (100% active)
|  |  | or | 24.84 | kg/d
|  | Ammonia solution concentration |  | 5 | % | Commercial Solution Concentration
|  | Ammonia solution consumption |  | 20.7 | L/hr
|  |  | or | 496.8 | L/day
|  | Metering Pump Operating Flow Rate |  | 20.7 | L/hr
|  | Metering Pump Operating Load |  | 50 | %
|  | Calculated Pump Capacity |  | 41.4 | L/hr
|  | Number of Pumps in Operation |  | 1 | unit
|  | Rated Pump Capacity per Unit |  | 41.4 | L/hr
| Selection | Actual Pump Capacity |  | 50 | L/hr
|  | Pump Head per Unit |  | 13 | bar
|  | Actual Number of Pumps |  | 2 | units | 1 in operation，1 standby, automatic control
| Process Calculations | Chemical Tank Retention Time |  | 1 | day
|  | Chemical Tank Storage Capacity |  | 496.8 | L
|  | Actual Storage Capacity per Tank |  | 500 | L
|  | Number of Tanks in Operation |  | 1 | unit
| Selection | Design Storage Capacity per Tank |  | 500 | L
|  | Actual Number of TanksTank |  | 1 | unit | 1 in operation，0standby