## Sheet1
Chemical Dosing System Calculation Sheet
Equipment Name:Antiscalant Dosing Skid
Basic information:
|  | Feed Water FlowQwater: | 200 | m3/h |  | Chemical Name: | 阻垢剂
|  | Chemical Dosage (X): | 5 | mg/l | Prepared Solution Concentration (η): |  | 20%
|  | Average Daily Dosing Time (t): | 24 | h/d | Solution Density (ρ): |  | 1200 | g/L
|  | Dosing Interval (T): | 3 | d | Product Concentration (ηraw) |  | 100%
Calculation information:
|  |  | Formula |  |  | Calculated Value | Selected Value
| 100% Active Chemical Consumption (M1): |  | M1=Qwater*X/1000 |  |  | 1 |  | kg/h
| Commercial Product Consumption (M2): |  | M2=M1/ηraw |  |  | 1 |  | kg/h
| Prepared Solution Consumption (M3): |  | M3=M1/η |  |  | 5 |  | kg/h
| Dosing Water VolumeQwater: |  | Qwater=（M3-M2）*t/1000 |  |  | 0.096 |  | m3/d
| Metering Pump Flow Qpump: |  | Qpump=M3*1000/ρ |  |  | 4.1667 |  | L/h
| Solution Tank Volume (V): |  | V=Qpump*t*T/1000 |  |  | 0.3 |  | m3
| Monthly Product Consumption (My): |  | My=M2*t*30/1000 |  |  | 0.72 |  | 吨
Equipment Name:Sodium Bisulfite (NaHSO₃) Dosing Skid
Basic information:
|  | Feed Water FlowQwater: | 200 | m3/h |  | Chemical Name: | 亚硫酸氢钠NaHSO3
|  | Chemical Dosage (X): | 3 | mg/l | Prepared Solution Concentration (η): |  | 20%
|  | Average Daily Dosing Time (t): | 24 | h/d | Solution Density (ρ): |  | 1380 | g/L
|  | Dosing Interval (T): | 7 | d | Product Concentration (ηraw) |  | 98%
Calculation information:
|  |  | Formula |  |  | Calculated Value | Selected Value
| 100% Active Chemical Consumption (M1): |  | M1=Qwater*X/1000 |  |  | 0.6 |  | kg/h
| Commercial Product Consumption (M2): |  | M2=M1/ηraw |  |  | 0.61224 |  | kg/h
| Prepared Solution Consumption (M3): |  | M3=M1/η |  |  | 3 |  | kg/h
| Dosing Water VolumeQwater: |  | Qwater=（M3-M2）*t/1000 |  |  | 0.057306 |  | m3/d
| Metering Pump Flow Qpump: |  | Qpump=M3*1000/ρ |  |  | 2.1739 |  | L/h
| Solution Tank Volume (V): |  | V=Qpump*t*T/1000 |  |  | 0.36522 |  | m3
| Monthly Product Consumption (My): |  | My=M2*t*30/1000 |  |  | 0.44082 |  | 吨
Equipment Name:UF Backwash Hydrochloric Acid (HCl) Dosing Skid
Basic information:
|  | Feed Water FlowQwater: | 450 | m3/h |  | Chemical Name: | HCl
|  | Chemical Dosage (X): | 100 | mg/l | Prepared Solution Concentration (η): |  | 10%
|  | Average Daily Dosing Time (t): | 0.14 | h/d | Solution Density (ρ): |  | 1100 | g/L
|  | Dosing Interval (T): | 7 | d | Product Concentration (ηraw) |  | 36%
Calculation information:
|  |  | Formula |  |  | Calculated Value | Selected Value
| 100% Active Chemical Consumption (M1): |  | M1=Qwater*X/1000 |  |  | 45 |  | kg/h
| Commercial Product Consumption (M2): |  | M2=M1/ηraw |  |  | 125 |  | kg/h
| Prepared Solution Consumption (M3): |  | M3=M1/η |  |  | 450 |  | kg/h
| Dosing Water VolumeQwater: |  | Qwater=（M3-M2）*t/1000 |  |  | 0.0455 |  | m3/d
| Metering Pump Flow Qpump: |  | Qpump=M3*1000/ρ |  |  | 409.0909 |  | L/h
| Solution Tank Volume (V): |  | V=Qpump*t*T/1000 |  |  | 0.40091 |  | m3
| Monthly Product Consumption (My): |  | My=M2*t*30/1000 |  |  | 0.525 |  | 吨
Equipment Name:RO Feed Hydrochloric Acid (HCl) Dosing Skid
Basic information:
|  | Feed Water FlowQwater: | 200 | m3/h |  | Chemical Name: | HCl
|  | Chemical Dosage (X): | 4 | mg/l | Prepared Solution Concentration (η): |  | 10%
|  | Average Daily Dosing Time (t): | 24 | h/d | Solution Density (ρ): |  | 1100 | g/L
|  | Dosing Interval (T): | 3 | d | Product Concentration (ηraw) |  | 36%
Calculation information:
|  |  | Formula |  |  | Calculated Value | Selected Value
| 100% Active Chemical Consumption (M1): |  | M1=Qwater*X/1000 |  |  | 0.8 |  | kg/h
| Commercial Product Consumption (M2): |  | M2=M1/ηraw |  |  | 2.2222 |  | kg/h
| Prepared Solution Consumption (M3): |  | M3=M1/η |  |  | 8 |  | kg/h
| Dosing Water VolumeQwater: |  | Qwater=（M3-M2）*t/1000 |  |  | 0.13867 |  | m3/d
| Metering Pump Flow Qpump: |  | Qpump=M3*1000/ρ |  |  | 7.2727 |  | L/h
| Solution Tank Volume (V): |  | V=Qpump*t*T/1000 |  |  | 0.52364 |  | m3
| Monthly Product Consumption (My): |  | My=M2*t*30/1000 |  |  | 1.6 |  | 吨
Equipment Name:Oxidant Dosing Skid (UF Backwash NaClO)
Basic information:
|  | Feed Water FlowQwater: | 450 | m3/h |  | Chemical Name: | NaClO
|  | Chemical Dosage (X): | 100 | mg/l | Prepared Solution Concentration (η): |  | 10%
|  | Average Daily Dosing Time (t): | 480 | s/d | Solution Density (ρ): |  | 1100 | g/L
|  | Dosing Interval (T): | 3 | d | Product Concentration (ηraw) |  | 10%
Calculation information:
|  |  | Formula |  |  | Calculated Value | Selected Value
| 100% Active Chemical Consumption (M1): |  | M1=Qwater*X/1000 |  |  | 45 |  | kg/h
| Commercial Product Consumption (M2): |  | M2=M1/ηraw |  |  | 450 |  | kg/h
| Prepared Solution Consumption (M3): |  | M3=M1/η |  |  | 450 |  | kg/h
| Dosing Water VolumeQwater: |  | Qwater=（M3-M2）*t/1000 |  |  | 0 |  | m3/d
| Metering Pump Flow Qpump: |  | Qpump=M3*1000/ρ |  |  | 409.0909 |  | L/h
| Solution Tank Volume (V): |  | V=Qpump*(t/3600)*T/1000 |  |  | 0.16364 |  | m3
| Monthly Product Consumption (My): |  | My=M2*(t/3600)*30/1000 |  |  | 1.8 |  | 吨
CIP Chemical Cleaning UnitCIP
Basic information:
| CIP Fill Volume Qwater: |  | 5 | m3 | CIP Fill Time (T): |  | 300 | S
Equipment Name:Oxidant Dosing Skid (CIP)
Basic information:
|  | Chemical Dosage (X): | 350 | mg/L | Concentrated Solution Density(η): |  | 10%
| Concentrated Solution Density (ρ): |  | 1.1 | kg/L |  | Pump Opening (n): | 80%
Calculation information: |  |  | Calculated Value |  |  | Note:Formula
| Metering Pump Flow Rate Qpump: |  | 238.6364 | L/h | Qpump=Qwater*X/1000/η/ρ/T*3600/n
Equipment Name:Acid Dosing Skid
Basic information:
|  | Chemical Dosage (X): | 0.04% | mg/mg | Concentrated Solution Density(η): |  | 10%
| Concentrated Solution Density (ρ): |  | 1.1 | kg/L |  | Pump Opening (n): | 80%
Calculation information: |  |  | Calculated Value |  |  | Note:Formula
| Metering Pump Flow Rate Qpump: |  | 272.7273 | L/h | Qpump=Qwater*X/η/ρ*1000/T*3600/n
Equipment Name:Caustic (Alkali) Dosing Skid
Basic information:
|  | Chemical Dosage (X): | 0.1% | mg/mg | Concentrated Solution Density(η): |  | 30%
| Concentrated Solution Density (ρ): |  | 1.3 | kg/L |  | Pump Opening (n): | 80%
Calculation information: |  |  | Calculated Value |  |  | Note:Formula
| Metering Pump Flow Rate Qpump: |  | 192.3077 | L/h | Qpump=Qwater*X/η/ρ*1000/T*3600/n