## UF Calculation
Number | Project | Value | Unit | Note
一、 | UF System
| Effective Membrane Area per /Element | 70 | m2
| Design Membrane Flux | 40 | LMH | Values Taken per Product Manual
| Total UF Permeate Flow (RO Feed) | 2708 | m3/h | Crossflow Filtration, Calculated Based on RO Feedwater
| Calculated Total Membrane Area Required | 67700 | m2
| Calculated Number of Membrane Elements Required | 967.1429 | Pieces
| Number of UF Trains Selected | 10 | Sets
| Membrane Area Required per UF Train | 6770 | m2
| Membrane Elements Required per UF Train | 96.7143 | Pieces
| Actual Number of Membrane Elements Installed per UF Train | 96 | Pieces
| Total Number of UF Membrane Elements Installed | 960 | Pieces
| Total Effective Membrane Area Installed | 67200 | m2
| Actual UF Membrane Flux | 40.2976 | LMH
二、 | UF Operation Design Calculation
| Filtration Time | 28.5 | min
| Air Scour Duration | 30 | s
| Backwash Time 1 | 20 | s
| Backwash Time 2 | 20 | s
| Forward Flush Duration | 20
| Operating Cycles per Day | 48.5393 | Times
| Actual Operating Hours per Day | 1383.3708 | min
| Continuous Production Capacity per UF Train | 270 | m3/h
| UF Actual Permeate Capacity per Hour (Excluding Backwash) | 281.0526 | m3/h
| Backwash Flux | 20 | LMH
| Backwash Flow per UF Train | 1.5 |  | Backwash Water Volume: 0.8–1.5 × Design Permeate Flow, per Membrane Supplier Manual
| Backwash Water Volume per Cycle(Times) | 0.1875 | m3
| Total Backwash Water Volume per 24 h | 9.1011 | m3
| Forward Flush Water Volume per Cycl（Times） | 1.5 | m3
| Total Forward Flush Water Volume per 24 h | 72.809 | m3
| Backwash Water Volume Averaged per Piece-hour | 0.37921 | m3
| Forward Flush Water Volume Averaged per Piece-hour | 3.0337 | m3
| Actual UF Permeate Capacity | 284.4656 | m3/h
| CIP Interval (Cleaning Cycle Period) | 30 | d
三、 | CIP Tank Calculation
| Fill Volume per Membrane Element | 0.071145 | m3 | Based on Membrane Element Length and Diameter
| Fill Volume per UF Train | 6.8299 | m3
| Membrane Element Volume Fraction | 30 | %
| Water Volume Required per UF Train | 4.7809 | m3
| CIP Piping Diameter | 150 | mm
| CIP Piping Length | 40 | m
| Water Volume in CIP Piping | 0.7065 | m3
| CIP Cartridge Filter Diameter | 350 | mm
| Effective Height | 1 | m
| CIP Cartridge Filter Housing Volume | 0.096162 | m3
| Cartridge Occupied Volume Fraction in Filter Housing | 5 | %
| Water Volume in Cartridge Filter Housing | 0.091354 | m3
| Calculated CIP Tank Volume | 5.5788 | m3
| Adjusted CIP Tank Volume (with Factor) | 6.6945 | m3
| CIP Tank Volume Considering Recirculation | 0.5 | m3
| Calculated CIP Tank Total Volume | 7.1945 | m3
| CIP Tank Sizing Volume | 4 | m3
四、 | UF CIP Chemical Dosing Tank Calculation
| NaClO Dosing Concentration | 50 | g/m3
| NaClO Dosage per Hour | 20.25 | kg/h
| Commercial Solution Concentration | 0.1
| NaClO 10% Solution Consumption | 202.5 | kg/h
| NaClO 10% Solution Volume | 184.0909 | L/h | Density of 10% NaClO Solution: 1.1 g/cm³
| Daily Dosing Duration | 0.13333 | h
| Required Daily Volume of NaClO 10% Solution | 24.5455 | L
| Metering Pump Operating Flow Rate | 184.0909 | L/h
| Metering Pump Duty | 50 | %
| Metering Pump Calculated Capacity | 368.1818 | L/h
| Chemical Tank Capacity Calculation (Total) | 0.44182 | m3
| Dosing Interval | 120 | h | Typical Requirement: >48–120 Hours
| Chemical Tank Sizing Capacity | 0.5 | m3
| NaOH Dosing Concentration | 3 | mg/L
| NaOH Dosage per Hour | 1.215 | kg/h | 100% Neat Chemical (As-supplied)
| Commercial Solution Concentration | 0.3
| NaOH 30% Solution Consumption | 4.05 | kg/h
| NaOH 30% Solution Volume | 2.9562 | L | Density of 30% NaOH Solution: 1.37 g/cm³
| Metering Pump Operating Flow Rate | 2.9562 | L/h
| Metering Pump Duty | 50 | %
| Metering Pump Calculated Capacity | 5.9124 | L/h
| Chemical Tank Sizing Capacity | 0.5 | m3
| HCl Dosing Concentration | 3 | mg/L
| HCl Dosage per Hour | 1.215 | kg/h | 100% Neat Chemical (As-supplied)
| Commercial Solution Concentration | 0.3
| HCl 30% Solution Consumption | 4.05 | L/h
| HCl 30% Solution Volume | 3.5248 | L | Density of 30% HCl Solution: 1.149 g/cm³
| Daily Dosing Duration | 0.1 | h
| Required Daily Volume of HCl 30% Solution | 0.35248 | L
| Metering Pump Operating Flow Rate | 3.5248 | L/h
| Metering Pump Duty | 50 | %
| Metering Pump Calculated Capacity | 7.0496 | L/h
| Chemical Tank Sizing Capacity | 0.5 | m3

## RO Calculation
Reverse Osmosis Calculation
Number | Project | Value | Unit | Note
一、 | RO Cleaning Tank
| Pressure Vessel Volume (6-element) /Single piece | 0.19409 | m3
| No. of Pressure Vessels | 16 | Vessels | Calculated by RO calculation software.
| Total Pressure Vessel Volume | 3.1055 | m3
| Volume Occupied by Membrane Elements (%) | 30 | %
| Water Volume inside Pressure Vessels | 2.1739 | m3 | Single piece
| Cleaning Piping Diameter | 150 | mm
| Distance | 30 | m
| Piping Hold-up Volume | 0.52987 | m3
| Cleaning Cartridge Filter Diameter | 400 | mm
| Effective Height | 1 | m
| Cleaning Cartridge Filter Volume | 0.1256 | m3
| Filter Cartridge Volume Occupancy | 5 | %
| Cartridge Filter Hold-up Volume | 0.11932 | m3
| Calculated Cleaning Tank Total Volume | 2.8231 | m3
| Tank Volume after Applying Coefficient | 3.3877 | m3 | The coefficient is taken as 1.2.
| Recirculation Allowance Volume in Tank | 0.5 | m3
| Final Required Cleaning Tank Volume | 3.8877 | m3
| Selected Cleaning Tank Capacity | 4 | m3
二、 | Cleaning Pump Calculation
| Cleaning Water Flow | 8 | m3/h
| No. of Stage-1 Feed Pressure Vessels | 16 | Vessels
| Cleaning Pump Flow Rate | 128 | m3/h
三、 | RO System Chemical Dosing Calculation
3.1 | Non-oxidizing Biocide Concentration | 5 | mg/L
| Biocide Dosage (every dosing) | 1.95 | kg/h
Commercial Product Concentration
| Non-oxidizing Biocide 10% Solution Consumption | 19.5 | L/h
| Metering Pump Operating Flow | 19.5 | L/h
| Metering Pump Load | 50 | %
| Calculated Pump Capacity | 39 | L/h
| Calculated Day Tank Volume (total) | 0.039 | m3
| Selected Day Tank Capacity | 0.5 | m3
3.2 | Reducing Agent Concentration | 5 | mg/L
| Reducing Agent Dosage (every day) | 46.8 | kg/d
| or | 1.95 | kg/h
| Reducing Agent 10% Solution Consumption | 19.5 | L/h
| or | 468 | L/d
| Metering Pump Operating Flow | 19.5 | L/h
| Metering Pump Load | 50 | %
| Calculated Pump Capacity | 39 | L/h
| Calculated Day Tank Volume | 1.1232 | m3
| Selected Day Tank Capacity (total) | 2 | m3
3.2 | Antiscalant Dosing | 3 | mg/L
| Antiscalant Dosage (Single set) | 9.36 | kg/d
| or | 0.39 | kg/h
| Antiscalant 10% Solution Consumption | 3.9 | kg/h | Density1.37
| Antiscalant 10% Solution Consumption | 2.8467 | L/h
| or | 68.3212 | L/d
| Metering Pump Operating Flow | 2.8467 | L/h
| Metering Pump Load | 50 | %
| Calculated Pump Capacity | 5.6934 | L/h
| Calculated Day Tank Volume | 0.49191 | m3
| Selected Day Tank Capacity (total) | 0.5 | m3